Specification for Automatic Sludge Blanket Meter

Application

Automatic measurement of sludge blanket levels in clarifiers, thickeners, etc. in water and wastewater treatment plants.

Sensor

The measuring principle is based on transmission of a single NIR (Near Infra-Red) light beam between two glass prisms and the ability of particles to absorb this light.  NIR light is not sensitive to color and does not contribute to biological growth as with visible light.  Light source to be 880 nm wavelength NIR light (reflective design sensors are not acceptable). The sensor should be lowered at programmable intervals or pulses from limit switch on rake until the sludge phase is found or blanket level detected.  The sensor is then raised and cleaned with a built-in water flushing system after each cycle.  The sensor head should be made of 316SS and attached to 33’ (10 m) of 4 conductor cable with Tefsel outer coating, in order to withstand mechanical wear and chemical attack from various fluids.

Transmitter - Control Box

The transmitter should be microprocessor based with self-instructing menu, digital circuitry, and illuminated LCD screen.  Sludge blanket height to be presented in feet on LCD display and as a scaleable 0/4-20 mA, 700 ohms, galvanically isolated, output signal, (8 bit resolution).  A second screen should be available to show to 240 data logged points as blanket depth versus time or solids concentration versus tank depth.  Output signal should be proportional to sludge blanket level. Second output to be RS485 communication to show solids concentration versus depth in tank.  Unit to be equipped with alarm relay.  The enclosure should be water-tight molded polyurethane, NEMA 4 (IP65).

The power supply must be equipped with filter, fuse and varistors for protection against power surges. The alarm contact is normally open (dry contact), when activated (closed contact) it should have max.resistive load of 250V/2A.  The transmitter should have EEPROM memory with battery backup for clock.  Following a power failure the sensor should return to home position and then resume operating without requiring recalibration. Power supply is to be 110/1/60.  Illuminated LCD display to continuously display current sludge blanket level in feet.  Housing to be equipped with built-in thermostat and heater to be activated at temperatures below 40(F.

Programming Module

Sounding intervals to be determined by internal timer or externally pulses from a rake.  Timer intervals to be adjustable from 4 ( 120 minutes.  Transmitter to have internal pulse counter that is adjustable from 1(99 pulses.  Pulses are generated by external closing relay, which is activated by the rake and powered by 5 VDC supplied by the control box.  Limit switch to be normally mounted 90 degrees out of phase with rake on circular clarifiers.

All programming and settings are performed from the outside of the transmitter box by using a self-instructing menu controlled by just four touch pad keys.  Unit to accept two calibrations points: 1) zero point using clean deaerated water and 2) sample point using RAS and entering concentration determined by lab.  In order to obtain a high accuracy on distance measurement, the unit should allow for calibration against a known distance between the probe’s “home position”  and a reference point.  Unit to have programming offset for dead zone in order to prevent floating sludge or foam from being detected as false sludge blanket.  Maximum span or travel distance to be 32’ from bottom of control box to bottom of tank.

Tamperproof programming feature is required to keep settings from being changed, except by authorized personnel.  In the case of power loss an EEPROM memory should save programming during power outages.

Self-Diagnostics

The software should be of Multi-task design.  It should also contain a watch-dog function connected to the microprocessor.  The software should inform the “watch-dog” at least once per second that the device is working properly.  If it does not, then the “watch-dog” shall restart the processor in order for the unit to resume measuring.

Winch

Winch assembly to consist of motor, 110/1/60, pvc winding drum and pvc weather-proof enclosure.  Winch to include flushing mechanism for probe and 1/2” npt (12 mm)  hose connection for flushing water.  Flushing intervals to be programmable.  Max. flush water pressure to be 90 psig (6 bar).  Winch to have safety clutch to prevent major damage in case of probe being caught in the rake.  Safety clutch to be adjustable from motor to winch drum.  Probe speed to 5.7” per second.  Sensor to have built-in tilt alarm, so sensor will return to home position, if it contacts the rake or any other item trip down.

Mounting

Sludge Blanket Monitor to be equipped with two (2) L shaped stainless steel brackets for 1.5” handrails (2” brackets) which can be hung directly on a handrail.   Optional 4” & 6” L brackets should be available for angle handrail.

Warranty

The manufacturer shall warrant the equipment to be free of defects from workmanship and material for a period of one (1) year after shipment.

Supplier

Specification is written around equipment manufactured by Cerlic Controls, AB,

Model – CAT-µP, P/N 12705248  Phone  404-256-3097 or Fax  404-256-3094

File: SPEC/CAT.DOC                                                                                              7/02  Rev. 7