Specification for Suspended Solids Meters in WTP

Application

Continuous on-line measurement of suspended solids in a water treatment plant from 0-20% concentration for influent river water for alum dosing, clarifier underflow, sand filter backwash control, and thickened or conditioned sludge to a press.

Sensor

The measuring principle is based on transmission of a single NIR (Near Infra-Red) light beam  generated by a light emitting diode (LED) and received by a silicon detector. NIR light is not sensitive to color and does not contribute to biological growth as with visible light.  Suspended solid concentrations are measured as a function of the ability of suspended materials to absorb and reflect NIR-light (near infra-red).  Sensors based on “reflection” of light by particles are not acceptable.  Sensor to have built-in liquid temperature and light emitting diode compensation loops to maintain constant light source.

The sensor housing is to be made of 316SS with sapphire lenses designed for 365 psig operating pressure.  Sensor to have 1” NPT male connection on both ends and contraction at lens to ¾” to obtain a self-cleaning of lens.   Minimum flow requirement as specified below to maintain turbulent flow.  Fluid can flow through sensor in either direction.    Sensor to be supplied with 33’ (10 m) of shielded 11 conductor cable with polyurethane jacket and plastic military connector with o-ring seal.  The sensor should have a measuring range as specified below.

Solids Range      Sensor Type                Gap            Required Flow

0-3%              CT20/25                      ¾’              8-10 gpm

0-20%            CT03/25                     1/8”              3-5 gpm

Signal Processor Transmitter Box

Microprocessor based transmitter with self-instructing menu, digital circuitry, and illuminated graphical LCD display.  Graphical display to show solids concentrations in ppm, mg/l or % solids and 0-100% of mA output as well as temperature of light emitting diode.  Graphical display to show high & low alarm set points, calibration points and current suspended solids concentration.  The same control box should be used for in-line and by-pass sensors, to reduce spare parts.  The control box produces a linearized 4-20 mA, max 700 ohms galvanically isolated, output signal (12 bit resolution) proportional to suspended solids concentrations.  Unit to contain programmable relay to alarm for solids concentrations at high and low set points or faulty sensor.  Light on front panel to indicate status of alarm.  To avoid fluctuating output  signal, the control box should have a dampening feature or integration time which can be set from 1 to 59 seconds.  The enclosure should be water-tight molded polyurethane box, NEMA 4 (IP65).  The power supply must be equipped with filter, fuse and varistors for protection against power surges.  The alarm contacts are normally open (dry contact), when activated (closed contact) they should have max. resistive load of 250V/2A.  The control box should have EEPROM memory.  Following a power failure the control box should start up and resume measuring without requiring recalibration.  Power supply is to be 110/1/60.

Self-Diagnostics

The software should be of Multi-task design.  It should also contain a watch-dog function connected to the microprocessor.  The software should inform the “watch-dog” at least once per second that the device is working properly.  If it does not, then the “watch-dog” shall restart the processor in order for the unit to resume measuring.

Programming Module

All programming and settings are performed from the outside of the control box by using a self-instructing menu, controlled by just four touch pad keys.   Unit to have HELP key to assist operator in programming.  Special plug-in proms or manually adjustable potentiometers for programming are not acceptable.  Tamperproof programming feature is required to keep settings from being changed, except by authorized personnel.  In the case of power loss, an EEPROM memory should save programming during power outages.

Zero point calibration to be done using clean, deaerated water.  The control box should allow for calibration against suspended solids solutions by calibrating to one point or up to five points for wide calibration range.  Any of these five points may be entered and the unit shall calculate the correlation between the points.  The values for the calibration points which are obtained from laboratory analysis, should be able to be entered anytime after calibration since the meter correlates these to light transmission values.  Graph scale should be adjustable by changing 4(20 mA output settings.  Sample points should not have to be re-entered to change scale.  Programming menus to be of a cursor type.

Mounting

Sensor to be supplied with 1” SS male NPT connections.  Control box can be mounted outside, but must not be exposed to direct sunlight.  The transmitter should have four (4) 5/16” holes with rubber bushings for mounting to wall or mounting plate.  If the temperature should be less than 32(F (0(C) for extended periods then the transmitter should be mounted in a special housing or inside.

Warranty

The manufacturer shall warrant the equipment to be free of defects from workmanship and material for a period of one (1) year after shipment.

Supplier

Specification is written around equipment manufactured by Cerlic Controls, AB,

Phone  404-256-3097 or Fax  404-256-3094

Model – CT20/25/CSP-(P,  P/N 24501, for 0-3% solids

Model – CT03/25/CSP-µP, P/N 24511, for 0-20% solids

File: SPEC/CT0325.DOC                                                                                           9/00   Rev. 1